## 9_May_Workshop_Overview
Setting the Scene / A primary goal of the EPNRWG's HTR Workstream is to ensure that the HTR provide a single minimum technical standard for generation and network equipment on all interconnected networks in the Pilbara. / Members have provided a list of existing issues and gaps in the HTR, which were compiled and provided to PAC on 18 April 2024. / EPWA proposes that the issues in the long list can be categorised as 'governance' or 'technical', with governance framework items (including compliance and enforcement of standards, and change management of standards) are best suited to the PNR workstream; allowing this group to focus on technical issues related to minimum standards.
Today's workshop / In conjunction with the ISO, EPWA has prepared for discussion (refer to tab Work Plan_Under Development): / - A draft description of each issue / - An indicative priority (High/Moderate/Low) for each issue / - A preliminary assessment of the effort involved (simple or substantive) / - Categorisation of issues as 'goverance' or 'technical' / Outcomes sought from 9 May 2024 workstream meeting / 1. Confirm intention for a single minimum standard for interconnected Pilbara networks / 2. Agree governance issues to be addressed in PNR workstream, with this group (HTR workstream) to focus on the content of technical standards / 3. Agree description of issue; indicative priority; effort involved for each of the 46 issues raised / 4. Identify a responsible party(ies) to lead development of options for working group consideration
Future workstream meetings (11 July; 12 September; 14 November) / Pending outcomes from 9 May meeting, the remaining three scheduled HTR workstream meetings will consider options for HTR issues raised. / Depending on the issue: / - the responsible party may develop a proposed solution, or may come up with initial options to bring back to the group for further discussions; or / - it may be that issues are parked for inclusion as a piece of work to do on the implementation plan (to be published in February 2025).

## Work_Plan_Under_Development
OG #	Issue #	Description of Issue	Priority	Simple or Substantive	Governance or Technical	Submitter
8	1	NSP to NSP connection arrangements in the HTR and accountabilities. Right now the Rules only reference NSP to Applicant, which results in confusion when it is NSP to NSP connections via tie lines.	High	Simple	Governance	Rio Tinto
19	2	Equipment ratings and the cost of consumed ratings - how are costs managed when upgrades are necessary; whether the last project pays.	High	Simple	Governance	Rio Tinto
5	3	Definition of contingency events versus credible contingency events and how this may flow on to pre-contingent events. The definition of credible contingency events currently doesn’t align with the AEMC definition which relates credible to things like weather conditions and present threats.	High	Substantive	Technical	Rio Tinto
9	4	Consider requirements to update voltage and frequency standards in accordance with proposed legislative changes to voltage and frequency requirements.	High	Substantive	Technical	Horizon Power
10	5	Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including review of the target frequency recovery times under Section 2.2.1 (25 minutes at 48 Hz) may have adverse impacts on system security.	High	Substantive	Technical	Horizon Power
11	6	Frequency variations - do we need to lower the single contingency event limit due to increasing penetration of renewables / less system inertia e.g. NT has 47 Hz.	High	Substantive	Technical	ISO
18	7	Consider requirements for NSPs to specify NWIS power system strength requirements and complete necessary assessments as renewable penetrations increases to ensure power system security.	High	Substantive	Goverance & Technical	BHP, ISO, Rio Tinto
23	8	Consider wholistic review of the treatment of Battery Energy Storage Systems and inverter based generating units, including clarity on which sections of the rules apply for these generating units.	High	Substantive	Technical	Horizon Power, ISO
24	9	Reference to grid forming and grid following inverter technology may be helpful, with specific regard to the differences in the technical performance between the differing technologies. A definition here may be helpful as there doesn’t appear to be a clear definition on what is grid forming, grid following, or what has virtual synchronous generator performance.	High	Substantive	Technical	Rio Tinto
25	10	Additional requirements for dynamic performance on asynchronous inverter connected generation e.g. damping capability for reactive power and active power control systems for inverter connected generation.	High	Substantive	Technical	BHP
26	11	Additional requirements for inverter connected generation response to power system disturbances, such as required magnitude of reactive current injection/absorption to support the power system during and post power system disturbances.	High	Substantive	Technical	BHP
27	12	Requirements for storage devices to provide network support services (frequency and voltage support) when operating in load/charging mode to enhance power system security/flexibility. Currently the HTR requires storage devices to act as consumer equipment when withdrawing power from the network.	High	Substantive	Technical	BHP
31	13	Definition and use of 'energisation' vs 'commercial operations' is inconsistent throughout the HTR and PNR. Clarity is required about the process and what actions are required from each party at which stage. / Inclusion of data to be submitted with connection applications (See Horizon Power Tech Rules Sections 3.3.2, 3.4.3, 3.6.5, and Attachments 3-10).	High	Substantive	Governance & Technical	Horizon Power, ISO
32	14	Renewable generation could comply, but the requirement of 460 ms ride through is overly onerous. We suggest this is revisited system wide to test suitability given it is inconsistent with other countries. / The interpretation of the wording should be clarified as it is not clear if this a requirement or optional (Western Power historically tested compliance with this an equivalent clause with some flexibility in the interpretation).	High	Substantive	Technical	BP
33	15	Currently requirement is for up to 4 Hz per second. This requirement has been updated in the WEM Rules.	High	Substantive	Technical	BP, ISO
34	16	Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: / - Review Section 3.3.3.3(f) - Absorption of reactive power is helpful under some circumstances and may be required for longer periods. Review clause in context of new operating environment. / - Most OEMs struggle to achieve the requirement for any pre-fault absorption of reactive power to be terminated within 200 ms after clearing of the fault. Further, from a system perspective, it would not be optimal if all generators stop absorbing after 200 ms. / - The WEM Rules have changed this clause (as did the proposed updated to the WP TR).	High	Substantive	Technical	Horizon Power
35	17	It is not prudent for the system if all generators follow this requirement simultaneously. / This clause has been changed in the WEM Rules. Further, we note that some wind generators have not been able to meet this requirement.	High	Substantive	Technical	BP
37	18	This is currently 0.05 Hz. The point at which the dead band is measured is unclear in the current drafting and needs to be updated. The WEM Rules have been revised to be +/-0.025 Hz around 50.0 Hz (refer to A12.6.1.9).	High	Substantive	Technical	BP
38	19	The identified rate of response is difficult for some OEMs of non-dispatchable generating units to achieve – the current requirement is achieving 90% within 2 seconds and new output to be sustained for no more than 10 seconds. / The minimum requirement of WEM rules (12.6) states asynchronous machines to meet 60% of the freq response in 6 seconds and 90% by 15 seconds. / Related clauses in the WEM Rules to consider are: / – A12.6.3.2 which provides more achievable requirements than the current Pilbara HTR. / – A provision for negotiating the standard is requested.	High	Substantive	Technical	BP
45	20	Improve definition of metering obligations for managing EBAS obligations.	High	Substantive	Governance & Technical	Horizon Power
46	21	How ESS costs are to be allocated (noting at the PAC Meeting 29.02.2024, the ISO advised that nominations would be called for a separate working group to be formed on this issue).	High	Substantive	Governance	Rio Tinto
20	22	Consider requirements regarding disturbance monitoring and synchrophasors.	Moderate	Simple	Technical	Horizon Power
28	23	Consider update to Figure 3.3 noting the four-quadrant capability of inverters.	Moderate	Simple	Technical	Horizon Power
29	24	Clarify treatment of ambient temperatures in the context of Section 3.3.3.1. Clarify distinction of using ‘nameplate’ vs ‘derated capacity’ when determining which set of generator compliance rules should apply.	Moderate	Simple	Technical	Horizon Power
30	25	The temperature dependency is a critical factor in the Pilbara that is not adequately considered in the Pilbara HTR. The higher temperatures in the Pilbara will affect the generator’s ability to comply with maximum output requirements (or the maximum output that can be expected). / Reactive power related requirements are linked to temperature, whereas historical versions of the rules including the current Pilbara HTR have not linked active power to temperature. This issue should be resolved in the Pilbara HTR to allow the network operator to have a more realistic understanding of what the generation is able to and expected to achieve. / In the WEM, wind farms struggle to meet the reactive power capability requirements at 40 degrees (for example A12.2.3.2). However, WEM Rules are more realistic where consideration of temperature is concerned. / Of note: / – Reactive power capability in clause 3.3.3.1 on possible map with locations and ambient temperature. / – Active power capability might need to be de-rated for the wind and solar farms above certain temperatures. This may be a gap in the existing Pilbara HTR as we were unable to identify the relevant clause. / – Recommend a review of clauses that refer to “ambient temperature” in addition to the above to ensure suitability.	Moderate	Simple	Technical	BP
36	26	Inclusion of Monitoring and Control Requirements (See Horizon Power Tech Rules Section 3.3.4).	Moderate	Simple	Governance	Horizon Power
40	27	Consider requirements for pole slip protection, e.g. where Critical Fault Clearance tRme issues exist.	Moderate	Simple	Technical	Horizon Power
44	28	Review of fault level management on the system: / - Consider minimum fault rating requirements for Transmission plant at significant network nodes, and fault level management. / - Consider potential requirements for limitations on maximum fault levels on the system and consider providing guidance on the calculation of fault levels. Define credible versus ultimate case.	Moderate	Simple	Technical	Horizon Power, Rio Tinto
1	29	Consider requirements adequacy of black start requirements/arrangements.	Moderate	Substantive (study likely)	Technical	Horizon Power
2	30	Connection Point Compliance parameters and definition (including negotiated vs ideal rules - with particular consideration for brownfield plant vs greenfield). / Consider if any updates required to facilitate or improved the treatment of Connection Point Compliance measures.	Moderate	Substantive	Governance & Technical	Horizon Power, Rio Tinto
13	31	Resolve responsibilities for determination of power transfer limits.	Moderate	Substantive	Governance	Horizon Power
15	32	Update Critical Fault Clearing Times at Dampier and Cape Lambert 33kV to reflect recent system changes and approved derogations.	Moderate	Substantive (study likely)	Technical	ISO, Rio Tinto, Horizon Power
16	33	Overall review of visit of maximum fault clearance times to ensure alignment. Currently there is misalignment between Western Power, Horizon Power and Rio Tinto technical rules.	Moderate	Substantive (study likely)	Technical	Rio Tinto
17	34	ROCOF and include df/dt for under frequency load shedding and/or under frequency islanding. Determine if df/dt is used for islanding only, or if it can apply to ufls too.	Moderate	Substantive	Technical	Rio Tinto
21	35	Requirements on NSPs to enact special protection schemes to manage network congestion/instability as required to enhance system security. However, this shouldn’t be the sole option to manage security issues – network augmentation and re-dispatch are other methods by which this can be achieved. / Generators and loads to possess compliant control systems to facilitate operation of required network special protection schemes to be specified in connection agreements.	Moderate	Substantive	Goveranance	BHP
22	36	Requirements for generation to ride through multiple consecutive power system disturbances including minimum number of disturbances rode through within a specific period.	Moderate	Substantive	Technical	BHP
41	37	Inclusion of Testing requirements and test details for connection of Generating Units (See Horizon Power Tech Rules Attachment 11). / Dispatchable and non-dispatchable generator testing and compliance requirements and R2 model validation. What are the non-dispatchable unit testing requirements, and how does this differ to dispatchable units.	Moderate	Substantive	Technical	ISO, Horizon Power, Rio Tinto
42	38	Requirements for NSP to verify integrity of the UFLS scheme across the NWIS network via periodic tests and publish an annual performance report based test results and actual power system UFLS events, this will provide confidence to all customers of UFLS performance integrity and power system security.	Moderate	Substantive	Governance	BHP
3	39	Align with SWIS / other network operators.	Low	Simple	Governance	Rio Tinto
4	40	Overall review of referenced standards, noting that some standards have more recent versions than those referenced.	Low	Simple	Technical	Horizon Power
6	41	Better clarity required for definitions of distribution feeder / interconnector / tie (undefined but included in HTR Table 2.10).	Low	Simple	Technical	ISO, Rio Tinto
7	42	HTR 2.3.2e describes 'essential system services' to be put last for load shedding - however this is different to the defined essential system services ESS as defined in PNR. / Similarly throughout the HTR "ancillary service" is used instead of "essential service" - the PNR and HTR should be aligned with this terminology to avoid confusion.	Low	Simple	Governance	ISO
12	43	Is accumulated synchronous time error still required? Has been removed from NEM.	Low	Simple	Technical	ISO
14	44	Definition of “back-up protection systems” for tie lines. Does this mean main & backup, or does this mean duplicate main protection.	Low	Simple	Technical	Rio Tinto
39	45	Model guidelines and interaction of modelling guidelines with the HTR. How to ensure there are no mismatches in models.	Low	Simple	Technical	Rio Tinto
43	46	The existing Pilbara HTR offers disconnection as the primary means of dealing with non-compliance. There would be benefit for all parties if negotiation mechanisms were provided for that allow for re-testing and rectification of non-compliance without disconnection. This would enable parties to identify the causes of any performance issues and work together to solve them and continue operation where this is within acceptable risk limits given the unique non-compliance or performance issues. / Sections in the Horizon Power TR A11.6 relate to these mechanisms where testing is concerned. Further work at both the Pilbara HTR and the various NSP TRs could be needed to achieve more optimal outcomes.	Low	Simple	Governance	BP

## Initial_Submissions_Received
OG #	Consolidated Issue #	Rule	Topic	Description of Issue	Submitter
8	1	1.8.1(b)	Interconnection points	NSP to NSP connection arrangements in the HTR and accountabilities. Right now the Rules only reference NSP to Applicant, which results in confusion when it is NSP to NSP connections via tie lines.	Rio Tinto
19	2	3.2.1(f)	Cost of upgrades	This may not fall into the HTR, but it relates to equipment ratings and the cost of consumed ratings. How are costs managed when upgrades are necessary, does the last project pay?	Rio Tinto
5	3	1.5	Definitions	Definition of contingency events versus credible contingency events and how this may flow on to pre-contingent events. The definition of credible contingency events currently doesn’t align with the AEMC definition which relates credible to things like weather conditions and present threats.	Rio Tinto
9	4	2.2	Power system performance standards	Consider requirements to update voltage and frequency standards in accordance with proposed legislative changes to voltage and frequency requirements.	Horizon Power
10	5	2.2.1	Power system performance standards	Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: / Review the target frequency recovery times under Section 2.2.1 - 25 minutes at 48 Hz may have adverse impacts on system security.	Horizon Power
11	6	2.2.1	Power system performance standards	Frequency variations - do we need to lower the single contingency event limit due to increasing penetration of renewables / less system inertia e.g. NT has 47 Hz	ISO
18	7	3	System strength	Include system strength assessments into the HTR and associated guidance on how to do that.	Rio Tinto
18	7	3	System strength	Requirements for NSPs to specify NWIS power system strength requirements and complete necessary assessments as renewable penetrations increases to ensure power system security.	BHP
18	7	3	System strength	System strength assessment and remediation requirements	ISO
23	8	3.3	Inverter generating units	Consider wholistic review of the treatment of Battery Energy Storage Systems and inverter based generating units, including clarity on which sections of the rules apply for these generating units.	Horizon Power
23	8	3.3	Inverter generating units	Applicability of this section to BESS	ISO
23	8	3.7	New Connections	Requirements for connection of storage facilities	ISO
24	9	3.3	Inverter generating units	Reference to grid forming and grid following inverter technology may be helpful, with specific regard to the differences in the technical performance between the differing technologies. A definition here may be helpful as there doesn’t appear to be a clear definition on what is grid forming, grid following, or what has virtual synchronous generator performance.	Rio Tinto
25	10	3.3	Inverter generating units	Additional requirements for dynamic performance on asynchronous inverter connected generation e.g. damping capability for reactive power and active power control systems for inverter connected generation.	BHP
26	11	3.3	Inverter generating units	Additional requirements for inverter connected generation response to power system disturbances, such as required magnitude of reactive current injection/absorption to support the power system during and post power system disturbances.	BHP
26	11	3.6.7	Power factor requirements	Load power factor requirements	ISO
27	12	3.3	Inverter generating units	Requirements for storage devices to provide network support services (frequency and voltage support) when operating in load/charging mode to enhance power system security/flexibility. Currently the HTR requires storage devices to act as consumer equipment when withdrawing power from the network.	BHP
31	13	3.3.2, 3.4.3, 3.6.5, Attachments	New Connections	Inclusion of data to be submitted with connection applications (See Horizon Power Tech Rules Sections 3.3.2, 3.4.3, 3.6.5, and Attachments 3-10).	Horizon Power
31	13	4.1.3 / 4.2.5 / Attachment 11 & 12 / PNR 255, 269, 270, 274D, 274H	New Connections	Definition and use of 'energisation' vs 'commercial operations' is inconsistent throughout the HTR and PNR. Clarity is required about the process and what actions are required from each party at which stage.	ISO
32	14	3.3.3.3(c)	Immunity to voltage excursions	Renewable generation could comply, but the requirement of 460 ms ride through is overly onerous. We suggest this is revisited system wide to test suitability given it is inconsistent with other countries. / The interpretation of the wording should be clarified as it is not clear if this a requirement or optional (Western Power historically tested compliance with this an equivalent clause with some flexibility in the interpretation).	BP
33	15	3.3.3.3(d)	ROCOF	Currently requirement is for up to 4 Hz per second. However, a requirement of up to 1 to 2 Hz is more realistic. / This requirement has been updated in the WEM Rules. In A12.7.3.2, the minimum requirements are reasonable and requires a RoCoF to: / – reach 2 Hz/s over 250 milliseconds during the disturbance, or / – reach 1 Hz/s over 1 second during the disturbance. / Subject to further studies with the new renewables in service the exact number (1 to 2 Hz) could be clarified and rationale for what is achievable identified.	BP
33	15	3.3.3.3(d)	ROCOF	ROCOF - 4 Hz/s	ISO
34	16	3.3.3.3(f)	Post-fault reactive power of a power station with non-synchronous generating units	Most OEMs struggle to achieve the requirement for any pre-fault absorption of reactive power to be terminated within 200 ms after clearing of the fault. Further, from a system perspective, it would not be optimal if all generators stop absorbing after 200 ms. / The WEM Rules have changed this clause (as did the proposed updated to the WP TR). The new clause in A12.9 is more appropriate.	BP
34	16	3.3.3.3(f)	Post-fault reactive power of a power station with non-synchronous generating units	Wholistic review of power system ride through requirements, and performance and restoration for major disturbances, including: / Review Section 3.3.3.3(f) - Absorption of reactive power is helpful under some circumstances and may be required for longer periods. Review clause in context of new operating environment.	Horizon Power
35	17	3.3.3.3(h)	Continuous uninterrupted operation	It is not prudent for the system if all generators follow this requirement simultaneously. / This clause has been changed in the WEM Rules. Further, we note that some wind generators have not been able to meet this requirement.	BP
37	18	3.3.4.4(d)	Dead band	This is currently 0.05 Hz. The point at which the dead band is measured is unclear in the current drafting and needs to be updated. The WEM Rules have been revised to be +/-0.025 Hz around 50.0 Hz (refer to A12.6.1.9).	BP
38	19	3.3.4.4(f)	Rate of response	The identified rate of response is difficult for some OEMs of non-dispatchable generating units to achieve – the current requirement is achieving 90% within 2 seconds and new output to be sustained for no more than 10 seconds. / The minimum requirement of WEM rules (12.6) states asynchronous machines to meet 60% of the freq response in 6 seconds and 90% by 15 seconds. / Related clauses in the WEM Rules to consider are: / – A12.6.3.2 which provides more achievable requirements than the current Pilbara HTR. / – A provision for negotiating the standard is requested.	BP
45	20	PNR 138	Metering	Improve definition of metering obligations for managing EBAS obligations	Horizon Power
46	21	PNR Chapter 8	ESS Costs	How ESS costs are to be allocated (noting at the PAC Meeting 29.02.2024, the ISO advised that nominations would be called for a separate working group to be formed on this issue)	Rio Tinto
20	22	3.2.3	Disturbance Monitoring	Consider requirements regarding disturbance monitoring and synchrophasors.	Horizon Power
28	23	3.3	Inverter generating units	Consider update to Figure 3.3 noting the four-quadrant capability of inverters.	Horizon Power
29	24	3.3.3.1	Temperature dependency	Clarify treatment of ambient temperatures in the context of Section 3.3.3.1. Clarify distinction of using ‘nameplate’ vs ‘derated capacity’ when determining which set of generator compliance rules should apply.	Horizon Power
30	25	3.3.3.1 (reactive power capability), various others	Temperature dependency	The temperature dependency is a critical factor in the Pilbara that is not adequately considered in the Pilbara HTR. The higher temperatures in the Pilbara will affect the generator’s ability to comply with maximum output requirements (or the maximum output that can be expected). / Reactive power related requirements are linked to temperature, whereas historical versions of the rules including the current Pilbara HTR have not linked active power to temperature. This issue should be resolved in the Pilbara HTR to allow the network operator to have a more realistic understanding of what the generation is able to and expected to achieve. / In the WEM, wind farms struggle to meet the reactive power capability requirements at 40 degrees (for example A12.2.3.2). However, WEM Rules are more realistic where consideration of temperature is concerned. / Of note: / – Reactive power capability in clause 3.3.3.1 on possible map with locations and ambient temperature. / – Active power capability might need to be de-rated for the wind and solar farms above certain temperatures. This may be a gap in the existing Pilbara HTR as we were unable to identify the relevant clause. / – Recommend a review of clauses that refer to “ambient temperature” in addition to the above to ensure suitability.	BP
36	26	3.3.4	Monitoring and Control Requirements	Inclusion of Monitoring and Control Requirements (See Horizon Power Tech Rules Section 3.3.4).	Horizon Power
40	27	3.4.10.2	Pole slip	Consider requirements for pole slip protection, e.g. where critical fault clearance time (CFCT) issues exist.	Horizon Power
44	28	5.4.1	Power System Fault Levels	Fault level credible scenarios, definition of what is credible versus ultimate case. This relates to equipment rating, and can relate to 100% generation being online and running when that is not a scenario that is possible. This relates to max fault current contribution calculation method for equipment rating and its methodology.	Rio Tinto
44	28	5.4.1	Power System Fault Levels	Review of fault level management on the system: / Consider minimum fault rating requirements for Transmission plant at significant network nodes, and fault level management. / Consider potential requirements for limitations on maximum fault levels on the system and consider providing guidance on the calculation of fault levels.	Horizon Power
1	29	-	Black Start	Consider requirements adequacy of black start requirements/arrangements.	Horizon Power
2	30	-	Connection Point Compliance	Connection Point Compliance parameters and definition (including negotiated vs ideal rules - with particular consideration for brownfield plant vs greenfield)	Rio Tinto
2	30	-	Connection Point Compliance	Consider if any updates required to facilitate or improved the treatment of Connection Point Compliance measures.	Horizon Power
13	31	2.3.7, 2.3.8	Power transfer limits	Resolve responsibilities for determination of power transfer limits (Sections 2.3.7 - 2.3.8)	Horizon Power
15	32	2.6.4	Maximum total fault clearance times	Maximum total fault clearance times for 33kV tie lines are incorrect. Previous study suggested 365ms is the correct value, though some recent studies were carried out between HP and RTIO on this.	Rio Tinto
15	32	2.6.4	Maximum total fault clearance times	Update Critical Fault clearing times at Dampier and Cape Lambert 33kV to reflect recent system changes and approved derogations.	Horizon Power
15	32	2.6.4	Maximum total fault clearance times	Maximum fault clearing time for HP-RTIO tie line	ISO
16	33	2.6.4	Maximum total fault clearance times	Overall review of visit of maximum fault clearance times (CFCT’s) to ensure alignment. Currently there is misalignment between Western Power, Horizon Power and Rio Tinto technical rules.	Rio Tinto
17	34	2.4	ROCOF	ROCOF and include df/dt for under frequency load shedding and/or under frequency islanding. Determine if df/dt is used for islanding only, or can this apply to ufls too?	Rio Tinto
21	35	3.2.6 (b)	Protection	Requirements on NSPs to enact special protection schemes to manage network congestion/instability as required to enhance system security. However, this shouldn’t be the sole option to manage security issues – network augmentation and re-dispatch are other methods by which this can be achieved. / Generators and loads to possess compliant control systems to facilitate operation of required network special protection schemes to be specified in connection agreements.	BHP
22	36	3.3	Generation ride through	Requirements for generation to ride through multiple consecutive power system disturbances including minimum number of disturbances rode through within a specific period.	BHP
41	37	4	Testing	Dispatchable and non-dispatchable generator testing and compliance requirements and R2 model validation. What are the non-dispatchable unit testing requirements, and how does this differ to dispatchable units.	Rio Tinto
41	37	Attachment 11	Testing	Inclusion of Testing requirements and test details for connection of Generating Units (See Horizon Power Tech Rules Attachment 11).	Horizon Power
42	38	4	Testing	Requirements for NSP to verify integrity of the UFLS scheme across the NWIS network via periodic tests and publish an annual performance report based test results and actual power system UFLS events, this will provide confidence to all customers of UFLS performance integrity and power system security.	BHP
3	39	-	Rules Alignment	If there is opportunity for aligning the various N.O. Technical Rules into common for users.	Rio Tinto
3	39	-	Rules Alignment	Alignment of the HTR with the SWIS technical rules.	Rio Tinto
4	40	-	Standard references	Consider update of flicker, harmonics, and power quality standards to latest version of relevant standards i.e. AS/NZS 61000.3.	Horizon Power
4	40	-	Standard references	Overall review of referenced standards, noting that some standards have more recent versions than those referenced.	Horizon Power
6	41	1.5	Definitions	Interconnection definition in the Rules currently refers to transmission lines, however a tie line isn’t necessary considered as a transmission line. Refining this definition with regard to 33kV tie lines will provide more clarity.	Rio Tinto
6	41	1.5	Definitions	Better clarity required for definitions of distribution feeder / interconnector / tie (undefined but included in HTR Table 2.10).	ISO
7	42	1.5	Definitions	HTR 2.3.2e Describes 'essential system services' to be put last for load shedding - however this is different to the defined essential system services ESS as defined in PNR. / Similarly throughout the HTR "ancillary service" is used instead of "essential service" - the PNR and HTR should be aligned with this terminology to avoid confusion.	ISO
12	43	2.2.1b	Power system performance standards	Is accumulated synchronous time error still required? Has been removed from NEM	ISO
14	44	2.6.2, Definitions	Protection	Definition of “back-up protection systems” for tie lines. Does this mean main & backup, or does this mean duplicate main protection.	Rio Tinto
39	45	3.3.9, 3.6.12	Model	Model guidelines and interaction of modelling guidelines with the HTR. How to ensure there are no mismatches in models.	Rio Tinto
43	46	4 / potential new section	Flexibility to negotiate when issues are identified post-testing	The existing Pilbara HTR offers disconnection as the primary means of dealing with non-compliance. There would be benefit for all parties if negotiation mechanisms were provided for that allow for re-testing and rectification of non-compliance without disconnection. This would enable parties to identify the causes of any performance issues and work together to solve them and continue operation where this is within acceptable risk limits given the unique non-compliance or performance issues. / Sections in the Horizon Power TR A11.6 relate to these mechanisms where testing is concerned. Further work at both the Pilbara HTR and the various NSP TRs could be needed to achieve more optimal outcomes.	BP